# MODEL SPECIFICATION

# HELICAL PILE FOUNDATIONS

# SCOPE

## The work consists of designing, furnishing, and installing helical piles and load transfer devices used to support compression and tension loads according to the project Plans and these specifications. The parties and contract terms referred to in this specification are as follows:

## The Owner is the person or entity that owns the structure or will own the structure once it is completed. The Owner may have contractual agreements with, and be represented by, other parties such as engineers, architects or contractors that perform services under the direction of the Owner. Where Owner is used in this specification, it refers to the Owner or the Owner’s contracted representatives, separate from the Installing Contractor.

### The Installing Contractor installs and tests (if necessary) the helical piles and may perform other tasks associated with the project.

## The Pile Designer is the individual or firm hired by the Installing Contractor or Owner to design the helical piles.

## The Plans refer to the contract documents, including, but not limited to, the drawings and specifications for the project.

## The work may include helical pile load testing.

## The Owner will be responsible for obtaining any right-of-way or easement access permits necessary for the helical pile installation.

## Unless otherwise noted, the Installing Contractor shall provide all labor, tools, equipment, and materials necessary to accomplish the work.

## The Owner will provide suitable access to the construction site for the Installing Contractor’s personnel and equipment.

## Unless specifically noted otherwise in the contract documents, the Owner will remove and replace any structures, utilities, pavements, landscaping, or other surficial improvements in the work area as necessary to facilitate the work.

## The Owner will be responsible for overall construction oversight to preclude the development of unsafe conditions.

## The Owner will be responsible for field survey of the helical pile locations prior to helical pile installation and a post installation survey to determine pile shaft cutoff elevations (if necessary).

## The work does not include any post-construction monitoring of pile performance unless specifically noted otherwise in the contract documents.

# references

## American Institute of Steel Construction (AISC)

### AISC 360: Specification for Structural Steel Buildings

## American Society for Testing and Materials (ASTM)

### ASTM A29: Steel Bars, Carbon, and Alloy, Hot-Wrought

### ASTM A123: Zinc Coating (Hot-Dip) Coatings on Iron and Steel Products

### ASTM A153: Zinc Coating (Hot-Dip) on Iron and Steel Hardware

### ASTM A325: Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength

### ASTM A500: Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes

### ASTM A513: Electric-Resistance Welded Carbon and Alloy Steel Mechanical Tubing

### ASTM A572: High-Strength Low-Alloy Columbian-Vanadium Structural Steel

### ASTM B633: Electrodeposited Coatings of Zinc on Iron and Steel

### ASTM B695: Coatings of Zinc Mechanically Deposited on Iron and Steel

### ASTM D1143: Deep Foundations Under Static Axial Compressive Load

### ASTM D3689: Deep Foundations Under Static Axial Tensile Load

## International Code Council Evaluation Services (ICC-ES)

### Acceptance Criteria 358 (AC358): Acceptance Criteria for Helical Pile Systems and Devices

## Society of Automotive Engineers (SAE)

### SAE J429: Mechanical and Material Requirements for Externally Threaded Fasteners

# DEFINITIONS

## The following terms apply to helical piles used to support compression and tension loads:

## Allowable Strength Design (ASD): A structural and geotechnical design methodology which states that the summation of the actual estimated loads (nominal loads) must be less than or equal to the allowable strength. Allowable strength is obtained by dividing a nominal resistance (strength) by an appropriate factor of safety.

## Bearing Stratum: The soil layer (or layers) that provides the helical pile end-bearing capacity through load transfer from the helix plates.

## Crowd: Axial compressive force applied to the helical pile shaft as needed during installation to ensure the pile advances at a rate approximately equal to the helix pitch for each revolution.

## Design Load: The combined nominal loads using ASD methodology.

## Design Strength: A term used in structural design which is defined as the product of the nominal strength and the applicable resistance factor. An equivalent term typically used in geotechnical design is also sometimes referred to as factored resistance (Load and Resistance Factor Design).

## Extension Section: Helical pile shaft sections connected to the lead section or other extension sections to advance the helix plates to the required bearing depth. Plain extensions (without helix plates) or helical extensions (with one or more helix plates) may be used depending upon soil conditions or project requirements.

## Factor of Safety: The ratio of the ultimate pile capacity or nominal resistance (strength) to the nominal or service load used in the design of any helical pile component or interface (Allowable Stress Design).

## Factored Load: The product of a nominal load and an applicable load factor (Load and Resistance Factor Design).

## Factored Resistance: The product of a nominal resistance and an applicable resistance factor (Load and Resistance Factor Design).

## Geotechnical Capacity: The maximum load or the load at a specified limit state, which can be resisted through the pile’s interaction with the bearing soils (see also Ultimate Pile Capacity).

## Helical Pile: Consists of a central steel shaft with one or more helix-shaped bearing plates and a load transfer device (bracket) that allows attachment to structures. Helical piles are installed into the ground by application of torque and axial compressive force (“crowd”).

## Helix (Helical) Plate: Round steel plate formed into a helical spiral and welded to the central steel shaft. When rotated in the ground, the helix shape provides thrust along the pile’s longitudinal axis, thus aiding in pile installation. The plate transfers axial load to the soil through bearing.

## Helix Pitch: The distance measured along the axis of the shaft between the leading and trailing edges of the helix plate.

## Lead Section: The first helical pile shaft component installed into the soil. It consists of one or more helix plates welded to a central steel shaft.

## Limit State: A condition beyond which a helical pile component or interface becomes unfit for service and is judged to no longer be useful for its intended function (serviceability limit state) or to be unsafe (ultimate limit state (strength)).

## Load and Resistance Factor Design (LRFD): A structural and geotechnical design methodology that states that the Factored Resistance (Design Strength) must be greater than or equal to the summation of the applied factored loads.

## Load Factor: A factor that accounts for the probability of deviation of the actual load from the predicted nominal load due to variability of material properties, workmanship, type of failure and uncertainty in the prediction of the load (Load and Resistance Factor Design).

## Load Test: A process to test the ultimate pile capacity and relation of applied load to pile head movement by application of a known load on the helical pile head and monitoring movement over a specific time period.

## Loads: Forces that result from the weight of all building materials, occupants and their possessions, environmental effects, differential movement, and restrained dimensional changes. Permanent loads are those loads in which variations over time are rare or of small magnitude. All other loads are variable loads (see also Nominal Loads).

## Mechanical Strength: The maximum load or the load at a specified limit state that can be resisted by the structural elements of a helical pile.

## Net Deflection: The total movement at the pile head minus the theoretical elastic deformation of the pile shaft during a load test.

## Nominal Loads: The magnitude of the loads specified, which include dead, live, soil, wind, snow, rain, flood, and earthquakes (also referred to as service loads).

## Nominal Resistance: The pile capacity at a specified ultimate limit state (Load and Resistance Factor Design). See Ultimate Pile Capacity.

## Nominal Strength: A term used in structural design which is defined as the structure or member capacity at a specified strength limit state. See Ultimate Pile Capacity.

## Resistance Factor: A factor that accounts for the probability of deviation of the actual resistance (strength) from the predicted nominal resistance (strength) due to variability of material properties, workmanship, type of failure and uncertainties in the analysis (Load and Resistance Factor Design).

## Service Loads: See “Nominal Loads” above.

## Ultimate Pile Capacity: The helical pile capacity based on the least capacity determined from applicable ultimate limit states for mechanical and geotechnical capacities.

# APPROVED HELICAL PILE MANUFACTURERS

## Supportworks®, Inc., 11850 Valley Ridge Drive, Papillion, NE 68046; Phone: (800) 281-8545; Fax: (402) 393-4002.

## Due to the specific requirements for design and manufacturing of helical piles, the piles shall be obtained from Supportworks®, Inc., or other qualified manufacturers with an approved equivalent product. A request to substitute any other manufactured helical product must be submitted to the Owner for review not less than seven (7) calendar days prior to the bid date. The request must include:

### Documentation of at least ten years of production experience manufacturing helical piles,

### Documentation that the manufacturer’s helical piles have been used successfully in at least five engineered construction projects within the last three years,

### Product acceptance by the local building code official(s) having authority over the project, and/or

### Current ICC-ES or IAPMO product evaluation report or complete description of product testing and manufacturing quality assurance programs used to assess and maintain product quality and determine product mechanical strength and geotechnical capacities.

# acceptable products

## Solid Square Shaft Helical Pile Models HA150 and HA175 and Hollow Round Shaft Helical Pile Models HP237, HP287, HP288, HP350 and HP450 manufactured in accordance with the requirements of Sections 5 and 6 of this specification.

## Solid round corner square shaft helical anchors may be used for tension only applications.

## Hollow round shaft helical piles shall be used to resist axial compression and/or tension loads. Round shaft helical piles are generally more resistant to bending or buckling over solid square shaft counterparts due to superior cross-sectional properties and coupling details and have the following requirements:

### Pile shaft sections shall be in full, direct contact within couplings so as to remove coupling bolts and coupling welds from the axial compression load path.

### Pile shafts and couplings shall have a fit-up tolerance of 1/16-inch or less.

## Helix plates shall meet the following geometry and spacing criteria to minimize soil disturbance:

### True helix-shaped plates that are normal to the shaft such that the leading and trailing edges are within ¼-inch of parallel.

### Helix pitch is 3-inches ± ¼-inch.

### All helix plates have the same pitch.

### Helix plates have generally circular edge geometry.

### Helix spacing along the shaft shall be between 2.4 and 3.6 times the helix diameter.

### Helix plates are arranged along the shaft such that they theoretically track the same path as the preceding plate.

# Materials

## Central Steel Shafts:

### Models HA150 and HA175: 1.50-inch (HA150) or 1.75-inch (HA175) solid, round-corner square (RCS) hot-rolled steel bars conforming to ASTM A29 with a minimum yield strength of 90 ksi and a minimum tensile strength of 115 ksi. Shaft torsional rating of 6,500 ft-lb (HA150) or 10,000 ft-lb (HA175).

### Models HP237, HP287 and HP288:  Shall be 2.375-inch outer diameter by 0.154-inch nominal wall thickness (HP237), 2.875-inch outer diameter by 0.203-inch nominal wall thickness (HP287) or 2.875-inch outer diameter by 0.276-inch nominal wall thickness (HP288), hollow structural section in conformance with ASTM A500 Grade B or C with a minimum yield strength of 60 ksi and a minimum tensile strength of 70 ksi. Shaft torsional rating of 2,500 ft-lb (HP237), 5,600 ft-lb (HP287) or 7,900 ft-lb (HP288).

### Model HP350: 3.500-inch outer diameter by 0.340-inch nominal wall thickness, hollow structural section in conformance with ASTM A500 Grade B or C with a minimum yield strength of 65 ksi, a minimum tensile strength of 75 ksi and a shaft torsional rating of 17,500 ft-lb.

### Model HP450: 4.500-inch outer diameter by 0.337-inch nominal wall thickness, hollow structural section in conformance with ASTM A500 Grade B or C with a minimum yield strength of 50 ksi, a minimum tensile strength of 60 ksi and a shaft torsional rating of 22,000 ft-lb.

## Helix Plates:

### Manufactured with ASTM A572 Grade 50 steel in accordance with ICC-ES AC358 conforming product specifications with the following thickness requirements:

#### HA150, HA175, HP287, HP288, and HP350: Helix plates with outer diameters of 6, 8, 10, 12 or 14-inches shall be 0.375-inches thick and 16-inch diameter helix plates shall be 0.500-inches thick.

#### HP237: Helix plates with outer diameters of 6, 8, 10, 12 or 14-inches shall be 0.313-inches thick and 16-inch diameter helix plates shall be 0.375-inches thick.

#### HP450: Helix plates with outer diameters of 8, 10, 12 or 14-inches shall be 0.375-inches thick and 16-inch diameter helix plates shall be 0.500-inches thick.

## Coupling Hardware:

### HA150 and HA175: Coupled with 0.750-inch standard hex bolts conforming to SAE J429 Grade 8 and jam nuts.

### HP237: Coupled with 0.625-inch standard hex bolts conforming to ASTM A325 and heavy hex jam nuts.

### HP287 and HP288: Coupled with 0.750-inch standard hex bolts conforming to SAE J429 Grade 5 and standard jam nuts.

### HP350: Coupled with 1.000-inch standard hex bolts conforming to SAE J429 Grade 5 and standard hex jam nuts.

### HP450: Coupled with 1.125-inch standard hex bolts conforming to SAE J429 Grade 5 and standard hex jam nuts.

## Material Finish:

### Central Steel Shaft and Helix Plates: Shall be either plain steel or hot-dip galvanized in accordance with ASTM A123.

### Coupling Hardware: Bolts and nuts shall be mechanically galvanized in accordance with ASTM B695 (HA150 and HA175), hot-dip galvanized per ASTM A153 (HP237) and electrozinc plated per ASTM B633 (HP287, HP288, HP350, and HP450).

# design and performance requirements

## Helical piles shall be designed to support the specified compression, and tension loads as shown on the project Plans. The overall length, helix configuration and minimum torsional resistance of a helical pile shall be such that the required geotechnical capacity is developed by the helix plate(s) in an appropriate bearing stratum.

## All structural steel pile components shall be designed within the limits provided by the American Institute of Steel Construction (AISC) Specification for Structural Steel Buildings (AISC-360). Either Allowable Stress Design (ASD) or Load and Resistance Factor Design (LRFD) are acceptable methods of analysis. Product testing in accordance with ICC-ES Acceptance Criteria 358 may also be considered as an acceptable means of establishing system capacities.

## Except where noted otherwise on the project Plans, all piles shall be installed to provide an ultimate torque-correlated soil capacity based on an ASD or LRFD analysis. For ASD, a minimum factor of safety of 2 applied to the service or nominal loading shall be required. When an LRFD analysis is required, the Owner shall provide applicable pile design information including but not limited to; factored loads, resistance factors, and/or the required ultimate pile capacity. Factors of safety (ASD) or resistance factors (LRFD) may require modification to meet specific deflection criteria stated on the Plans or drawings.

## The required ultimate torque-correlated soil capacity shall be verified at each pile location by monitoring and recording the final installation torque and applying default torque correlations per ICC-ES AC358. Site-specific torque correlation factors may be determined by field load testing as specified in Section 14.

## Except where noted otherwise on the project Plans, each pile shall be designed to meet a corrosion service life of 50 years in accordance with ICC-ES AC358.

## The pile design shall consider group efficiency from pile spacing, pile buckling potential, and minimum helix plate depths in accordance with ICC-ES AC358.

# qualifications of installing contractor and Pile designer

## The Installing Contractor and/or Pile Designer shall submit the documentation required in this Section to the Owner. Work shall not begin until all the submittals have been received and approved by the Owner.

## Evidence of Installing Contractor’s competence in the installation of helical piles shall be provided to the Owner’s satisfaction and may include the following:

### A list of at least three projects completed within the previous three years wherein the Installing Contractor installed helical piles. The list shall include names and phone numbers of those project representatives who can verify the Installing Contractor’s participation in those projects.

### A letter from the pile manufacturer or manufacturer’s representative expressing ability and intent to provide on-site supervision of the pile installation.

## Evidence of Pile Designer’s competence shall be provided to the Owner’s satisfaction and may include the following:

### Registration as a Professional Engineer or recognition by the local jurisdictional authority.

### A list of at least three pile projects completed within the previous three years by the Pile Designer. The list shall include names and phone numbers of those project representatives who can verify the Pile Designer’s participation in those projects.

# pre-construction submittals

## Within 2 weeks of receiving the contract award, the Installing Contractor and/or Pile Designer shall submit the following helical pile design documentation to the Owner:

## Certification from the Pile Designer that the proposed piles meet the requirements of this specification.

## Qualifications of the Installing Contractor and Pile Designer per Section 8.

## Product designations for helical lead and extension sections and all ancillary products to be supplied at each helical pile location.

## Individual pile nominal axial loads, factors of safety, and LRFD load and resistance factors where applicable.

## Manufacturers published allowable system capacities for the proposed pile assemblies including shaft torsional ratings.

## Theoretical geotechnical end-bearing capacity of the piles and minimum pile termination torque requirements.

## Minimum and/or maximum embedment depths or other site-specific embedment depth requirements as may be appropriate for the site soil profiles.

## Installation angle and location tolerance requirements.

## Load test procedures and acceptance criteria, if applicable.

## Copies of certified calibration reports for torque measuring equipment and load test measuring equipment to be used on the project. The calibrations shall have been performed within one year of the proposed helical pile installation starting date.

## Provide proof of insurance coverage as stated in the project Plans and/or contract.

# placement requirements

## Helical piles shall be installed within 3-inches of the indicated plan location.

## Helical pile shaft alignment shall be within 2-degrees of the inclination angle shown on the Plans.

# pile installation

## Installing Contractor shall furnish and install all helical piles per the project Plans and approved pile design documentation. In the event of conflict between the project Plans and the approved pile design documentation, the Installing Contractor shall not begin construction on any affected items until such conflict has been resolved.

## The Installing Contractor shall conduct their construction operations in a manner to ensure the safety of persons and property in the vicinity of the work. The Installing Contractor’s personnel shall comply with safety procedures in accordance with OSHA standards and any established project safety plan.

## The Owner shall request marking of underground utilities by an underground utility location service as required by law, and the Installing Contractor shall avoid contact with all marked underground facilities.

## The portion of the construction site occupied by the Installing Contractor, including equipment and material stockpiles, shall be kept clean and orderly.

## Installation of helical piles may be observed by representatives of the Owner for quality assurance purposes. The Installing Contactor shall give the Owner at least 24 hours’ notice prior to the pile installation operations.

## The lead section shall be positioned at the location and batter angle as determined from the plan drawings and site survey.

## The helical pile sections shall be advanced into the soil in a continuous manner at a rate of rotation less than 25 revolutions per minute (rpm). Sufficient crowd shall be applied to advance the helical pile sections at a rate approximately equal to the pitch of the helix plate per revolution. The rate of rotation and magnitude of crowd pressure shall be adjusted for different soil conditions and depths. The piles shall be installed to meet the termination criteria in Section 12.

# termination criteria

## The minimum final torsional resistance and/or any required pile length or embedment depth criteria must be satisfied prior to terminating the pile installation. In the event any helical pile fails to meet the production quality control termination criteria, the following remedies may be suitable if authorized by the Owner:

## If the torsional resistance during installation reaches the helical pile’s allowable torque rating prior to satisfaction of the minimum embedment depth criterion:

### Terminate the installation at the depth obtained with the approval of the Owner, or

### Remove and replace the pile with one having a higher shaft torsional strength rating. The replacement pile must be installed to satisfy the minimum embedment depth criterion. It must also be embedded to a depth that places the uppermost helix plate at least three times its own diameter beyond where the lowest helix plate of the replaced pile was located without exceeding any applicable maximum embedment depth requirements and it must meet the minimum final torsional resistance criteria, or

### Remove and replace the pile with one having a different helix plate configuration. The replacement pile must be installed to satisfy the minimum embedment depth criterion. It must also be embedded to a depth that places the uppermost helix plate at least three times its own diameter below where the lowest helix plate of the replaced pile was located without exceeding any applicable maximum embedment depth requirements, and it must meet the minimum final torsional resistance criterion.

## If the installation reaches a specified maximum embedment depth without achieving the minimum torsional resistance criterion:

### Demonstrate acceptable pile performance through pile load testing, or

### De-rate the load capacity of the helical pile based on default or site-specific torque correlation factors and install additional piles with the approval of the Pile Designer and Owner. Additional piles must be installed at locations and batter angles that result in minimum helical plate spacings at bearing depth in accordance with ICC-ES AC358, or

### Remove and replace the pile with one having a different helix plate configuration. The replacement pile must be installed at least three times the largest helix plate diameter away from the original pile location. The new pile must satisfy the maximum embedment depth criterion and meet the minimum final torsional resistance criterion.

## If a helical pile fails to meet the acceptance criteria in a pile load test:

### Install the pile to a greater depth and installation torque and re-test; provided that, if a maximum embedment depth is specified, continued installation will not exceed the maximum embedment depth, or

### Replace the pile with one having more and/or larger helix plates. The replacement pile must be embedded to a depth that places the uppermost helix plate at least three times its own diameter below where the lowest helix plate of the replaced pile was located without exceeding any applicable maximum embedment depth requirements. The replacement pile must be re-tested, or

### De-rate the load capacity of the helical pile based on the results of the load test and install additional piles with the approval of the Pile Designer and Owner. Additional piles must be installed at locations and batter angles that result in minimum helical plate spacings at bearing depths in accordance with ICC-ES AC358.

# installation record submittals

## The Installing Contractor shall provide the Owner with copies of the individual helical pile installation records within 24 hours after each installation is completed. Formal copies shall be submitted within 30 days following the completion of the helical pile installation. These installation records shall include, but are not limited to, the following information:

## Date and time of installation

## Location of helical pile and pile identification number

## Installed helical pile model and helix plate configuration

## Termination depth and length of installed pile

## Installed inclination angle of the pile

## Final torsional resistance and torque correlated nominal geotechnical capacity based on final torsional resistance

## Comments pertaining to interruptions, obstructions, or other relevant information

# helical PILE testing

## Helical pile testing may consist of compression or tension testing in general conformance with the Quick Test methods of ASTM D1143 and ASTM D3689, respectively, and these specifications. The design load (DL) for testing shall be the combined nominal loads using ASD methodology unless stated otherwise in the Plan documents. The Owner shall specify the quantity, type, and location of the pile testing. The Installing Contractor shall furnish all labor, equipment, and material necessary to perform pile testing as shown on the Plans. The Installing Contractor shall submit a test plan to the Owner for review and approval prior to testing. No deviations from the approved test plan will be allowed without explicit approval in writing from the Owner.

## The test plan shall include, but not be limited to, the following information:

### The quantity and type of tests (compression or tension) and the proposed test locations.

### The pile test procedures and loading requirements in conformance with these specifications.

### The quantity, type, and accuracy of equipment used to apply the test load and monitor pile deflection.

### Calibration reports for any load application and monitoring equipment used in the load test such as dial or digital gauges, load cells, hydraulic cylinders, and pressure gauges.

## The load test equipment shall consist of:

### Calibrated dial or digital gauge(s) capable of measuring to 0.001-inch shall be mounted to an independent reference frame to measure pile movement.

### A hydraulic cylinder and pressure gauge calibrated as a unit shall be used to apply the test loads. The pressure gauge shall be graduated in 100 psi increments or less. The hydraulic cylinder shall have a nominal load capacity exceeding the maximum anticipated jack load by at least 20%. The cylinder maximum stroke shall have an additional 15% stroke length as anticipated for the test. A calibrated load cell may be used in place of the hydraulic cylinder and pressure gauge setup.

### A reaction frame shall be used to provide reaction for the test loads. The reaction frame shall be designed to minimize movement of the hydraulic cylinder during load application and to have the load application co-linear to the test pile, Compression and tension testing shall follow the reaction frame specifications in ASTM D1143 and ASTM D3689, respectively.

## Test procedures:

### Compression and tension testing shall be performed on sacrificial piles in general conformance with the Quick Test methods of ASTM D1143 and ASTM D3689, respectively, and the following criteria:

### Failure criteria shall be in accordance with ICC-ES AC358 and is when the net deflection exceeds 10% of the average helix plate diameter.

### An alignment load equal to 5 to 10% of the maximum anticipated test load may be applied prior to the start of the test to take out slack in the load test frame.

### Loading increments shall be performed at 5% of the anticipated maximum test load with a minimum hold time of 4 minutes at each increment.

### Upon completion of the maximum test load increment, the pile shall be unloaded in 5 to 10 even increments with minimum hold times of 4 minutes at each increment.

## Reporting requirements:

### Installing Contractor shall provide the Owner copies of raw field test data within 24 hours after the completion of each load test. Formal test reports shall be submitted within 30 days following test completion. Formal test reports shall include the following information:

### Name of project and Installing Contractor’s representative(s) present during load testing.

### Name of manufacturer’s representative(s) present during load testing, if any.

### Name of third-party test agency and personnel present during load testing, if any.

### Date, time, duration, and type of the load test.

### Unique test identifier and map showing the test pile location.

### Pile model and installation information including shaft type, helix configuration, lead and extension section quantities and lengths, angle of installation, final pile tip depth, installation date, total test pile length, and final termination torque.

### Calibration records for applicable pile installation and test equipment.

### Tabulated test results including cumulative pile head movement, loading increments and hold times.

### Plots showing load versus pile head movement for each loading/unloading interval.

# Cleanup

## Within one week of completion of the work, the Installing Contractor shall remove all material, equipment, tools, debris, or other items belonging to the Installing Contractor or used under the Installing Contractor’s direction.